## Slide 1
Application of High Efficiency Chillers in Hong Kong Baptist Hospital

## Slide 2: Introduction
Hong Kong’s History- Air Conditioning System
B. Background of Hong Kong Baptist Hospital
C. Retro-commissioning Plan
1. Replacement of Oil free chillers at Hong
Kong Baptist Hospital
2. Combination of Chiller Plant at Block DE
3. Interconnection of Chiller Plant at Block AB

## Slide 3
Hong Kong’s History- Air Conditioning System
Classroom
Hospital
Working Place
1960s
2000s

## Slide 4
Electricity Consumption in Hong Kong
Commercial Building
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 2 3 4 5 6 7 8 9 10 11 12 | 419 | 374 | 370 | 429 | 477 | 576 | 659 | 618 | 637 | 559 | 469 | 437
1980 | 1064 | 954 | 1006 | 1168 | 1279 | 1418 | 1618 | 1556 | 1559 | 1519 | 1302 | 1205
1990 | 2739 | 2657 | 2830 | 3078 | 3382 | 3901 | 4164 | 4242 | 4101 | 3836 | 3594 | 3056
 | 5612 | 5101 | 5465 | 5972 | 7016 | 7677 | 7741 | 8042 | 7737 | 7501 | 6513 | 5969
2010 | 6975 | 6396 | 7716 | 7494 | 8685 | 9458 | 10186 | 10043 | 9416 | 8576 | 7494 | 7445
2017 | 7211 | 6555 | 7492 | 7939 | 9336 | 10183 | 10447 | 10423 | 9953 | 9256 | 7665 | 7432
1970 15,950 TJ
1980 39,186 TJ
1990 85,553 TJ
2000 130,350 TJ
2010 150,307 TJ
2017 157,216 TJ
Month
Terajoule
1970s
2000s
Information Source: Census and Statistics Department
Summer Time

## Slide 5
Hong Kong’s Climate Action Plan 2030+
Information Source: Environmental Bureau

## Slide 6
Energy Saving Timeline for Government Buildings
(2013/14 data as baseline)
Energy Saving Plan for Hong Kong’s Built Environment (2015 – 2025 +)
Information Source: Environmental Bureau

## Slide 7
Retro-commissioning
“Retro-commissioning” is one of the key initiatives to promote energy saving for existing building.
Retro-commissioning (RCx) is a systematic process to periodically check an existing building’s performance to identify operational improvements that can save energy and thus lower energy bills and improve indoor environment.
Information Source: EMSD

## Slide 8: Background Hong Kong Baptist Hospital

## Slide 9: Hospital Development
1963
1979
1982
2008
2015
Block A
Block B
Block C
Block D
Block E
MRI Centre
Nuclear Medicine & PET Centre
257 Beds
320 Beds
111 Beds
94 Beds
102 Beds
Oncology Centre
OT
Skin & Laser Centre
ENT Centre
Eye Centre
Molecular Pathology Laboratory
Pharmacy
Radiotherapy
Heart Centre
Out-patient Centre
Specialist Centre
Pathology
ICU
Cardiac Catheterization Lab
Radiology
Specialist Centre
Pathology
Waterloo Road
Junction Road
Kam Shing Road
Block A
Block B
Block C
Block D
Block E

## Slide 10
Chart: 
Chart: 
| Chiller Plant | Air-conditioning | Lighting | Lift | Power | Fire Services
 | 55 | 20 | 12 | 2 | 10 | 1
Chart: 
| Chiller Plant | Chilled Water Pumps
欄1 | 80 | 20
Energy Use in Private Hospital

## Slide 11: Retro-commissioning Planning
2013
Replacement of Total 16 nos. Oil free chillers
2015
Combination of Chiller Plant at Block DE
2017
Interconnection of Chiller Plant at Block AB

## Slide 12: 1. Replacement of Oil free chillers at Hong Kong Baptist Hospital

## Slide 13: Oil free Chiller
Oil Free Magnetic Centrifugal Compressor
Oil Free Chiller
Magnetic Bearing System
Position Sensor ring
Motor
Motor rotor
Position sensor ring
Radial bearings
Axial bearing
Impellers
Radial bearings
13
Soft Starter
2.
1.

## Slide 14: Electricity Saving for Selection of Chiller
Chart: 
 | 7.8 | 5.8 | 4.6 | 3.3
 | 2.25 | 3.53 | 2.63 | 2.09
COP
Cooling Capacity (%)
Oil free Chiller
Air cool Chiller
10 20 30 40 50 60 70 80 90 100
IPLV | Oil free chiller | Air cool chiller
A. 25% | 7.8 | 2.25
B. 50% | 5.8 | 3.53
C. 75% | 4.6 | 2.63
D.100% | 3.3 | 2.09
 | 5.51 | 2.98

## Slide 15: Consideration on Replacement of Chillers
Need Improvement | Good | Excellent
1. High energy efficiency
COP
2.5 to 3.5
3.5 to 5
5 to 7
Water Cool Chiller
Air Cool Oil free Chiller
Air Cool Chiller
2. Maintenance Cost
High | Medium | Low
Air Cool Chiller
Air Cool Oil free Chiller
Water Cool Chiller

## Slide 16: Consideration on Replacement of Chillers
3. Weight
(Building Structure)
Heavy | Medium | Light
Air Cool Chiller
Air Cool Oil free Chiller
Water Cool Chiller
Micro Channel
4. Noise
Noisy | Fair | Quiet
Air Cool Chiller
Water Cool Chiller
Air Cool Oil free Chiller

## Slide 17
2014
Chiller B1
Chiller B2
2015
Chiller A1
2016
2017
Chiller B3,B4,B5
Chiller C1,C2, C3
Chiller M3
2018-2019
Chiller A3
Chiller B6
Chiller M1
Chiller M4
Chiller A2
Chiller A4
Replacement of Oil free Chillers
(2 Chillers, 1100 kW)
(3 Chillers , 2150 kW)
(2 Chillers, 580 kW)
(2 Chillers, 880 kW)
Building | Block A | Block B | Block Bext | Block C | Total
No. of Chiller | 4 | 6 | 3 | 3 | 16
kW | 1980 | 3130 | 2130 | 1800 | 9040
First Stage Analysis
Second Stage Analysis
(7 Chillers, 4000 kW)

## Slide 18
Replacement of Oil free Chillers
Block C
Block A
Block B

## Slide 19
Energy Saving of Replacement of Oil free Chillers at Block B and C
Chart: kWh
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
2012 | 235684.02 | 245036.89 | 356640.02 | 441325.95 | 506550.4 | 475076.82 | 521198.74 | 555700.06 | 486903.31 | 477444.46 | 391917.02 | 304497.42
2017 | 218016.45 | 173789.48 | 182364.87 | 240238.32 | 331287.01 | 362466.59 | 437100.4 | 444589.9 | 426233.14 | 384623.86 | 311664.06 | 208958.48
Saving in 2017 | 17667.57 | 71247.41 | 174275.15 | 201087.63 | 175263.39 | 112610.23 | 84098.34 | 111110.16 | 60670.17 | 92820.6 | 80252.96 | 95538.94
2016 | 195842.41 | 162696.6 | 197163.13 | 268611.4 | 375661.95 | 425044.25 | 393622.21 | 383149.88 | 353518.62 | 342060.24 | 255004.7 | 213358.73
Saving in 2016 | 39841.61 | 82340.29 | 159476.89 | 172714.55 | 130888.45 | 50032.57 | 127576.53 | 172550.18 | 133384.69 | 135384.22 | 136912.32 | 91138.69
2012 Baseline - 4,997,975 kWh
2017 - 3,721,332 kWh
2016 – 3,565,734 kWh
2012 Vs 2016
2012 Vs 2017
1,432,000 kWh
1,276,000 kWh
Energy Saving
(Record by CLP meter)
2,708,000 kWh

## Slide 20
Year | Saving | Saving (%) | kWh /Usable floor Area (m2)
2012 | Baseline | Baseline | 488
2013 | Renovation works for C7 and C8 and 2 nos. of chillers at Block B were completed. |  | 
2014 |  |  | 
2015 | Replacement of 9 nos. of chillers at Block B and C were completed. |  | 
2016 | 1,432,000 kWh | 28.7 % | 349
2017 | 1,276,000 kWh | 25.5 % | 364
Energy Saving for Chiller Plant at Block BC

## Slide 21
2. Combination of Chiller Plant at Block DE

## Slide 22: Electricity Saving of Combination of Chiller Plant at Block DE
Electricity Consumption
Month
Separate Two Chiller Plant for Block D and Block E
Combination of One Chiller Plant for Block D and Block E

## Slide 23: Combination of Chiller Plant at Block DE
Block D
Block E
Block D
Block E
Redevelopment
Chiller
Chiller
Chiller
Chiller
Chiller
Chiller
Chiller
Future
Expansion
2015
3 Nos. 600kW Screw Chillers
4 Nos.1100kW Oil Free Chillers

## Slide 24: Electricity Saving of Combination of Chiller Plant at Block D
Chart: 
2013 | 404217 | 397603 | 399039 | 448849 | 482171 | 603697 | 557099 | 546017 | 600118 | 509014 | 468685 | 380326
2017 | 326954 | 295441 | 278634 | 310027 | 296649 | 289000 | 313800 | 300067 | 298663 | 282994 | 285859 | 269315
Saving in 2017 | 77263 | 102162 | 120405 | 138822 | 185522 | 314697 | 243299 | 245950 | 301455 | 226020 | 182826 | 111011
kWh
Energy Saving
(Record by CLP meter)
2,249,000 kWh
2013 Baseline
2017
2013 Vs 2017
Notes: According to CLP online meter, the electricity consumption at Block D was reduced from 5,796,835 kWh in 2013 to 3,547,403 kWh in 2017. Therefore, the annual saving in 2017 was $2,249,000 in tariff .

## Slide 25: Electricity Saving of Combination of Chiller Plant at Block DE
 | Configuration | Total Cooling Capacity | Energy Saving for Combination of Chiller Plant at Block DE |  | 
 |  |  | 2013 (kWh) | 2017 (kWh) | Electricity Consumption for Chiller Plant (kWh)
Chiller Plant at Block D | 3 Nos. 600kW Screw Chillers | 1800kW | 5,796,835 | 3,547,403 | 2,249,432 by CLP Meter Record
Chiller Plant at Block E | 4 Nos. 1100kW Oil free Chillers | 4400kW | Redevelopment | 6,794,764 | Assumption by Calculation: 4 Nos. X 800 kW Screw type chillers for Block E = 2,181,362
 |  |  |  |  | Separate Two Chiller Plant for Block DE = 2,249,432+2,181,362 = 4,430,794 Actual Chillers Block DE at by BMS Record = 3,397,382 Total Saving = 4,430,794 - 3,397,382 = 1,033,422kWh

## Slide 26
3. Interconnection of Chiller Plant at Block AB

## Slide 27
Total Power Demand
Building Load
2 Chillers + 2 Pumps
1 Chiller + 1 Pump
Optimal Cooling Load Level for Switching On/Off Chillers and Associate Equipment
Electricity Saving for Optimal Cooling Load for Switching Chillers

## Slide 28
Interconnection of Chiller Plant at Block AB
Block A
Block B
Chiller
Chiller
Chiller
Chiller
2 Nos. 550kW Oil free Chillers
1 Nos. 680kW Oil free Chillers
1 Nos. 200kW Oil free Chillers
5 Nos. 550kW Oil free Chillers
Summer Mode
To Air Side Equipment
Chiller
Chiller
Chiller
Chiller
To Air Side Equipment
Chiller

## Slide 29
Interconnection of Chiller Plant at Block AB
Block A
Block B
Chiller
Chiller
Chiller
Chiller
2 Nos. 550kW Oil free Chillers
1 Nos. 680kW Oil free Chillers
1 Nos. 200kW Oil free Chillers
5 Nos. 550kW Oil free Chillers
Winter Mode/
Emergency Mode
To Air Side Equipment
Chiller
Chiller
Chiller
Chiller
To Air Side Equipment
Chiller

## Slide 30
New chilled water supply and return pipes to interconnect two chiller plants
Interconnection of Chiller Plant at Block AB
Control Logic
1. Total Cooling load of Block A and B < 80% Total Capacity of Chiller Plant B 2. Outdoor temperature is lower than 18oC
Shut down Chiller Plant A
Open one pair of inter connecting valve
Chilled Water Plant Supply by Block B
Keep on 30 mins
Plant B
Plant A

## Slide 31: Energy Saving of Interconnection of Chiller Plant at Block AB
 | Configuration | Total Cooling Capacity | Building load | Energy Saving for Interconnection at Block AB in Winter Season |  | 
 |  |  |  | Existing Arrangement | New Arrangement | Electricity Consumption
Chiller Plant at Block A | 1 Nos. 680kW and 200 kW Oil Free Chillers 2 Nos. 550kW Oil free Chillers | 1080kW | Summer: 864kW Winter: 250kW | 1 X 550kW Oil free Chillers 1 X Chilled Water Pump | Interconnection at Block AB was put in operation. | (106kW + 7.5 kW) X24 X 20 days X 3 months* = 163,440 kWh
Chiller Plant at Block B | 5 Nos. 550kW Oil free Chillers | 2750kW | Summer: 2200kW Winter: 800kW | 2 X 550kW Oil free Chillers 2 X Chilled Water Pump | 2 X 550kW Oil free Chillers 2 X Chilled Water Pump | Nil
Remark: Outdoor temperature is lower than 18oC in the winter season.

## Slide 32: Benefits A. Combination of Chiller Plant at Block DE B. Interconnection of Chiller Plant at Block AB
2.Energy Saving
4. Reduce Maintenance Cost
1. Reduce Noise Pollution
6. Improve Building Space Utilisation
5. Improve Reliability and Flexibility
3. Reduce Green House Gas Emission

## Slide 33: Electricity Consumption for Hong Kong Baptist Hospital in 2012 and 2017
Year | kWh | HK$ * | Indirect GHG emission in tonnes of CO2 equivalent
Block ABC |  |  | 
2012 | 20,199,960 | 20,805,959 | 11,716
2017 | 18,583,207 | 19,140,703 | 10,034
Saving | 1,616,753 | 1,665,256 | 1,682
Block DE |  |  | 
2013 | 4,430,792 | 4,563,716 | 2,792
2017 | 3,397,382 | 3,499,303 | 1,835
Saving | 1,033,422 | 1,064,412 | 957
Total | 2,650,175 | 2,729,668 | 2,639
114,000 Trees
Based on $1.03/kWh in 2017 for reference only.

## Slide 34: Appreciation
Gold Award in 2016
CLP Green Plus Award Public Organization & Utility Group
BEAM Plus Award (Block E)
(New Building V1.1)
Bronze Award in 2017

## Slide 35
Mission
Sustainable
Hospital

## Slide 36: Role of Engineer/ Facilities Manager
Get commitment
Understand
Plan & Organize
Implement
Control & Monitor
Feedback
Engineers / Facilities Manager can save the World.